# Example Data Summary Sheet for Wet Detention Basin Design

|  |  |
| --- | --- |
| **Design Element** | **Design Data** |
| **Site assessment data: (see attached maps)** |
| Contributing drainage area to basin (subwatershed A) | 120 acres |
| Distance to nearest private well (including off-site wells) | > 100 feet |
| Distance to municipal well (including off-site wells) | > 1200 feet |
| Ground slope at site of proposed basin | average 3% |
| Proposed outfall conveyance system/discharge (w/ distances) | 35 ft. to CTH “U” Road ditch1000 ft. to wetland |
| Any downstream roads or other structures? (describe) | Yes – 36” cmp road culvert |
| **Soil investigation data (see attached map & soil logs):** |
| Number of soil investigations completed | 3 (in basin area) |
| Do elevations of test holes extend 5 ft. below pond bottom? | Yes (see map) |
| Average soil texture at pond bottom elevation (USDA) | Clay loam |
| Distance from pond bottom to bedrock | > 5 feet |
| Distance from pond bottom to seasonal water table | Pond bottom 2 ft below mottlingNo water observed in test holes |
| **General basin design data (see attached detailed drawings):**  |
| Permanent pool surface area  | 1.5 acres |
| Design permanent pool water surface elevation | elev. 900.0  |
| Top of berm elevation (after settling) and width  | elev. 905.0 / 10 feet wide |
| Length/width (dimensions/ratio) | 445 ft. (L) x 145 ft. (W) = 3:1 |
| Safety shelf design (length, grade, max. depth) | 10 ft. @ 10% slope/1.5’ deepest |
| Liner yes/no, material, thickness | Not required due to clay loam soil |
| Ave. water depth (minus safety shelf/sediment) | 5 ft. (in center) |
| Sediment forebay size & depth | .16 acres (13% pool size)/5 feet |
| Sediment storage depth & design maintenance | 2 ft. depth for forebay & pool15 year maintenance schedule |
|  |
| Design Basin Inflow, Outflow & Storage Data **(see attached hydrographs and detail drawings)** |
| **Inflow Peak Flow** | MaximumOutflow Rate | **Max. Water Elevation**  | **Storage Volume** **at Max. Elev.**(above perm. pool) | **Outflow Control Structures\*** |
| 13 cfs(Post 1-yr./24 hr. peak) | .7 cfs(34 hr. drawdown) | 901.3 ft. | 2 acre feet | #1 |
| 23 cfs (Post 2-yr./24 hr. peak) | 11 cfs | 902.0 ft. | 3.1 acre feet | #1 and #2 |
| 84 cfs(Post 10-yr./24 hr. peak) | 35 cfs | 903.0 ft. | 4.5 acre feet | #3 |
| 272 cfs(Post 100-yr./24 hr. peak) | 123 cfs | 904.0 ft. | 6.0 acre feet | #3 and #4 |

\* **The controlling elements are summarized below (See attached detail drawing of outlet structure):**

 #1 = 6 inch orifice in water level control weir plate – flow line elev. @ 900.0 (1.3 ft. max. head)

 #2 = 2 foot wide rectangular weir – flow line elev. @ 901.3 (.7 ft. hydraulic head)

 #3 = 30 inch diameter smooth wall pvc pipe – flow line elev. @ 900.0 (3.0 ft. max. hydraulic head)

 #4 = 30 foot wide earthen/grass emergency spillway – flow line elev. @ 903.0 (1.0 ft. max. depth)

|  |
| --- |
| **Water Quality Data** |
| **Parameter** | **Units** | **Removal** |
| Total Suspended Solids | Lb / year | 81% |
| Total Phosphorus | Lb / year | 77% |